## 3PHT
PANEL |  | "A" |  |  |  | AUTO CALCULATIONS |  |  |  | CONNECTED AMPS | 133.3648
HIGH VOLTAGE |  | 208 | SYM RMS AMPS |  | 10000 | LOAD | 59580
LOW VOLTAGE |  | 120 | BREAKER TYPE |  | THQB | "D" DIVERSITY | -11590 |  |  | %FACTOR | 0
PHASE |  | 3 | MAIN BKR AMPS |  | NONE | 25% "C" LOAD | 0
HERTZ |  | 60 | FEED TOP/BOTTOM |  | TOP | TOTAL WATTS | 47990
NEUTRAL BUS Y/N |  | Y | MOUNTING |  | SURFACE | TOTAL KVA | 47.99
GROUND BUS Y/N |  | N | COVER TYPE |  | DOOR IN DOOR | CONN AMPS | 133.3648
GND WIRE Y/N |  | Y | MANUFACTURER |  | GE | FACTOR AMPS | 0 |  |  | COMPUTED AMPS | 133.3648
WIRE TYPE |  | THW |  |  |  | TOTAL AMPS | 133.3648
FED FROM |  | MSWBD | PANEL SIZE |  |  | DESIGN AMPS | 133.3648 |  |  | GROUND | Y | 1
# OF CIRCUITS |  | 42 | 200 AMPS |  |  | # OF CONDUITS | 1
MIN. AMPS |  | 0 |  |  |  | CONDUIT SIZE | 2"
% FACTOR | [5 empty] | # OF CABLES | 4
BUSSING |  | COPPER |  |  |  | SIZE OF CABLE | #1/0
ISOLATED GND |  | NO |  |  |  | SIZE OF GND | #6 |  |  | TYPE | THW | 1
[10 empty] | NETURAL | Y | 4
CIR # | BREAKER | CIRCUIT DESCRIPTION |  |  | L1 | L2 | L3 | DIVERSITY | CONTINUOUS | COLUMN SELECTION |  | 6
1 |  |  |  |  | 3600 | -------- | -------- | 0 | 0
3 | 30A-3P | FREEZER |  |  | -------- | 3600 | -------- | 0 | 0
5 |  |  |  |  | -------- | -------- | 3600 | 0 | 0
7 |  |  |  |  | -------- | -------- | -------- | 0 | 0
9 | 20A-3P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
11 |  |  |  |  | -------- | -------- |  | 0 | 0
13 |  |  |  |  | -------- | -------- | -------- | 0 | 0
15 | 20A-3P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
17 |  |  |  |  | -------- | -------- | -------- | 0 | 0
19 | 20A-1P | WAFFLE |  |  | 2400 | -------- | -------- | 0 | 0
21 | SPACE | SPACE |  |  | -------- | -------- | -------- | 0 | 0 | WIRES | 3
23 | 20A-1P | DISPLAY |  |  | -------- | -------- | 2400 | 0 | 0 | NETURAL | 1
25 | 20A-1P | SPARE |  |  | -------- | -------- | -------- | 0 | 0 | TOTAL | 4
27 | 20A-1P | RECEPTACLES |  | D | -------- | 2340 | -------- | 2340 | 0
29 | SPACE | SPACE |  |  | -------- | -------- |  | 0 | 0
31 | 20A-1P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
33 |  |  |  |  | -------- | -------- | -------- | 0 | 0
35 | 20A-3P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
37 |  |  |  |  | -------- | -------- | -------- | 0 | 0
39 | SPACE |  |  |  | -------- |  | -------- | 0 | 0
41 | SPACE |  |  |  | -------- | -------- |  | 0 | 0
CIR # | BREAKER | CIRCUIT DESCRIPTION |  |  | L1 | L2 | L3
2 |  |  |  |  | 3600 | -------- | -------- | 0 | 0
4 | 30A-3P | FREEZER |  |  | -------- | 3600 | -------- | 0 | 0
6 |  |  |  |  | -------- | -------- | 3600 | 0 | 0
8 |  |  |  |  | -------- | -------- | -------- | 0 | 0
10 | 20A-3P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
12 |  |  |  |  | -------- | -------- | -------- | 0 | 0
14 | 20A-1P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
16 | 20A-1P | SPARE |  |  | -------- | -------- | -------- | 0 | 0
18 | 20A-1P | RECEPTACLES |  | D | -------- | -------- | 2340 | 2340 | 0
20 | 20A-1P | RECEPTACLES |  | D | 2340 | -------- | -------- | 2340 | 0
22 | SPACE | SPACE |  |  | -------- |  | -------- | 0 | 0
24 | 20A-2P | COUNTER RECEPTACLES |  | D | -------- | -------- | 2340 | 2340 | 0
26 | 20A-2P |  |  | D | 2340 | -------- | -------- | 2340 | 0
28 | 20A-2P | SOFT SERVE RECEPTACLES |  | D | -------- | 2340 | -------- | 2340 | 0
30 | 20A-2P |  |  | D | -------- | -------- | 2340 | 2340 | 0
32 |  |  |  | D | 2000 | -------- | -------- | 2000 | 0
34 | 30A-3P | SOFT SERVE RECEPTACLES 1 |  | D | -------- | 2000 | -------- | 2000 | 0
36 |  |  |  | D | -------- | -------- | 2000 | 2000 | 0
38 |  |  |  | D | 3600 | -------- | -------- | 3600 | 0
40 | 30A-3P | SOFT SERVE RECEPTACLES 2 |  | D | -------- | 3600 | -------- | 3600 | 0
42 |  |  |  | D | -------- | -------- | 3600 | 3600 | 0
[8 empty] | 33180 | 0
[8 empty] | DIVERSITY | CONTINUOUS
CONDUCTOR AND CONDUIT SIZING DATABASE FOR THREE PHASE PANELS
SAMPLE DATABASE COPPER CONDUCTORS 75º C
[13 empty] | 1 |  | 2 |  | 3 |  | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[13 empty] | AMPS | SELECTED | #WIRES | SELECTED | WIRE | SELECTED | GND | SELECTED | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE
[13 empty] | 75º C | CONDUCTOR | PER | NUMBER OF | SIZE | GROUND | WIRE | CONDUIT | 4W W/G | 3W | 3W W/G | 3W | 3W W/G | 4W | 4W W/G | 4W | 4W W/G
[14 empty] | SIZE | PHASE | CONDUCTORS |  | SIZE | SIZE | SIZE | THW | THW | THW | THHN | THHN | THW | THW | THHN | THHN
[13 empty] | 65 | 0 | 1 | 0 | #6 | 0 | #8 | 0 | 1 1/4" | 1" | 1" | 3/4" | 3/4" | 1" | 1 1/4" | 3/4" | 1"
[13 empty] | 85 | 0 | 1 | 0 | #4 | 0 | #8 | 0 | 1 1/4" | 1" | 1 1/4" | 1" | 1" | 1 1/4" | 1 1/4" | 1" | 1 1/4"
[13 empty] | 100 | 0 | 1 | 0 | #3 | 0 | #8 | 0 | 1 1/4" | 1 1/4" | 1 1/4" | 1" | 1" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
|  | LOAD CALCULATIONS FOR PANEL |  | "A" | [8 empty] | 115 | 0 | 1 | 0 | #2 | 0 | #6 | 0 | 1 1/2" | 1 1/4" | 1 1/4" | 1" | 1 1/4" | 1 1/4" | 1 1/2" | 1 1/4" | 1 1/4"
[13 empty] | 130 | 0 | 1 | 0 | #1 | 0 | #6 | 0 | 2" | 1 1/4" | 1 1/2" | 1 1/4" | 1 1/4" | 1 1/2" | 2" | 1 1/2" | 1 1/2"
|  | CONNECTED LOAD LINE L1 |  |  |  | 19880 | [6 empty] | 150 | #1/0 | 1 | 1 | #1/0 | #6 | #6 | 2" | 2" | 1 1/2" | 1 1/2" | 1 1/4" | 1 1/2" | 2" | 2" | 1 1/2" | 1 1/2"
|  | CONNECTED LOAD LINE L2 |  |  |  | 17480 | [6 empty] | 175 | 0 | 1 | 0 | #2/0 | 0 | #6 | 0 | 2" | 1 1/2" | 2" | 1 1/2" | 1 1/2" | 2" | 2" | 2" | 2"
|  | CONNECTED LOAD LINE L3 |  |  |  | 22220 | [6 empty] | 200 | 0 | 1 | 0 | #3/0 | 0 | #6 | 0 | 2 1/2" | 2" | 2" | 1 1/2" | 2" | 2" | 2 1/2" | 2" | 2"
[13 empty] | 230 | 0 | 1 | 0 | #4/0 | 0 | #4 | 0 | 2 1/2" | 2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2" | 2 1/2"
|  | SUB TOTAL WATTS |  |  |  | 59580 | [6 empty] | 255 | 0 | 1 | 0 | 250 KCM | 0 | #4 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2" | 2 1/2" | 3" | 2 1/2" | 2 1/2"
[13 empty] | 285 | 0 | 1 | 0 | 300 KCM | 0 | #4 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
|  | RECEPTACLE LOAD |  |  | 33180 | [7 empty] | 310 | 0 | 1 | 0 | 350 KCM | 0 | #3 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
|  | LESS 1ST 10,000 WATTS |  |  | -10000 | [7 empty] | 335 | 0 | 1 | 0 | 400 KCM | 0 | #3 | 0 | 3" | 3" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[13 empty] | 380 | 0 | 1 | 0 | 500 KCM | 0 | #3 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | REMAINING WATTAGE |  |  | 23180 | [7 empty] | 400 | 0 | 1 | 0 | 500 KCM | 0 | #3 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | 50% OF THE REMAINING WATTAGE |  |  | 11590 | [7 empty] | 460 | 0 | 2 | 0 | #4/0 | 0 | #2 | 0 | 2 1/2" | 2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2" | 2 1/2"
[13 empty] | 510 | 0 | 2 | 0 | 250 KCM | 0 | #1 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 2 1/2" | 3" | 2 1/2" | 2 1/2"
|  | LESS RECEP DEMAND (PER Article 220-44 NEC) |  |  |  | -11590 | [6 empty] | 570 | 0 | 2 | 0 | 300 KCM | 0 | #1 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
[13 empty] | 620 | 0 | 2 | 0 | 350 KCM | 0 | #1/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
|  | CONTINUOUS LOAD |  |  | 0 | [7 empty] | 670 | 0 | 2 | 0 | 400 KCM | 0 | #1/0 | 0 | 3 1/2" | 3" | 3" | 2 1/2" | 3" | 3" | 3 1/2" | 3" | 3"
[5 empty] | X .25 | [7 empty] | 760 | 0 | 2 | 0 | 500 KCM | 0 | #1/0 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
[13 empty] | 855 | 0 | 3 | 0 | 300 KCM | 0 | #2/0 | 0 | 3" | 2 1/2" | 3" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
|  | PLUS 25% OF THE CONTINUOUS LOAD |  |  |  | 0 | [6 empty] | 930 | 0 | 3 | 0 | 350 KCM | 0 | #2/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[13 empty] | 1005 | 0 | 3 | 0 | 400 KCM | 0 | #3/0 | 0 | 3 1/2" | 3" | 3" | 2 1/2" | 3" | 3" | 3 1/2" | 3" | 3"
[13 empty] | 1140 | 0 | 3 | 0 | 500 KCM | 0 | #3/0 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | SUB TOTAL |  |  |  | 47990 | [6 empty] | 1240 | 0 | 4 | 0 | 350 KCM | 0 | #4/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[14 empty] | #1/0 |  | 1 |  | #6 |  | 2"
|  | FACTOR | 0 |  |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0
[14 empty] | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL WATTS |  |  |  | 47990 | [7 empty] | 0 |  | 0 |  | 0 |  | 0
[14 empty] | 0 |  | 0 |  | 0 |  | 0
AMPS
|  | 47990 | 208 |  | = | 133.3648 | [7 empty] | #1/0 |  | 1 |  | #6 |  | 2"
|  | LAST MODIFIED | 2022-09-01

## 1PHT
PANEL |  | "A" |  |  |  | AUTO CALCULATIONS |  |  |  | CONNECTED AMPS | 99.711
HIGH VOLTAGE |  | 240 | SYM RMS AMPS |  | 10000 | LOAD | 42810
LOW VOLTAGE |  | 120 | BREAKER TYPE |  | THQB | "D" DIVERSITY | -1410 |  |  | %FACTOR | 0
PHASE |  | 1 | MAIN BKR AMPS |  | NONE | 25% "C" LOAD | 0
HERTZ |  | 60 | FEED TOP/BOTTOM |  | TOP | TOTAL WATTS | 41400
NEUTRAL BUS Y/N |  | Y | MOUNTING |  | SURFACE | TOTAL KVA | 41.4
GROUND BUS Y/N |  | N | COVER TYPE |  | DOOR IN DOOR | CONN AMPS | 99.711
GND WIRE Y/N |  | Y | MANUFACTURER |  | GE | FACTOR AMPS | 0 |  |  | COMPUTED AMPS | 99.711
WIRE TYPE |  | THW |  |  |  | TOTAL AMPS | 99.711
FED FROM |  | MSWBD | PANEL SIZE |  |  | DESIGN AMPS | 99.711 |  |  | GROUND | Y | 1
# OF CIRCUITS |  | 42 | 200 AMPS |  |  | # OF CONDUITS | 1
MIN. AMPS |  | 0 |  |  |  | CONDUIT SIZE | 1 1/4"
% FACTOR |  | 0 |  |  |  | # OF CABLES | 2
BUSSING |  | COPPER |  |  |  | SIZE OF CABLE | #3
ISOLATED GND |  | NO |  |  |  | SIZE OF GND | #8 |  |  | TYPE | THW | 1
[10 empty] | NETURAL | Y | 4
CIR # | BREAKER | CIRCUIT DESCRIPTION |  |  | L1 | L2 |  | DIVERSITY | CONTINUOUS | COLUMN SELECTION |  | 6
1 |  |  |  |  | 3600 | -------- |  | 0 | 0
3 | 30A-3P | FREEZER |  |  | -------- | 3600 |  | 0 | 0
5 |  |  |  |  | -------- | -------- |  | 0 | 0
7 |  |  |  |  | -------- | -------- |  | 0 | 0
9 | 20A-3P | SPARE |  |  |  | -------- |  | 0 | 0
11 |  |  |  |  | -------- | -------- |  | 0 | 0
13 |  |  |  |  | -------- | -------- |  | 0 | 0
15 | 20A-3P | SPARE |  |  | -------- | -------- |  | 0 | 0
17 |  |  |  |  | -------- | -------- |  | 0 | 0
19 | 20A-1P | SPARE |  |  |  | -------- |  | 0 | 0
21 | SPACE | SPACE |  |  | -------- | -------- |  | 0 | 0 | WIRES | 1
23 | 20A-1P | DISPLAY |  |  | -------- | -------- |  | 0 | 0 | NETURAL | 1
25 | 20A-1P | SPARE |  |  |  | -------- |  | 0 | 0 | TOTAL | 2
27 | 20A-1P | RECEPTACLES |  | D | -------- | 2200 |  | 2200 | 0
29 | SPACE | SPACE |  |  | -------- | -------- |  | 0 | 0
31 | 20A-1P | SPARE |  |  | -------- | -------- |  | 0 | 0
33 |  |  |  |  | -------- | -------- |  | 0 | 0
35 | 20A-3P | SPARE |  |  | -------- | -------- |  | 0 | 0
37 |  |  |  |  | -------- | -------- |  | 0 | 0
39 | SPACE |  |  |  | -------- |  |  | 0 | 0
41 | SPACE |  |  |  | -------- | -------- |  | 0 | 0
CIR # | BREAKER | CIRCUIT DESCRIPTION |  |  | L1 | L2
2 |  |  |  |  | 3600 | -------- |  | 0 | 0
4 | 30A-3P | FREEZER |  | D | -------- | 3600 |  | 3600 | 0
6 |  |  |  |  | -------- | -------- |  | 0 | 0
8 |  |  |  |  | -------- | -------- |  | 0 | 0
10 | 20A-3P | SPARE |  |  | -------- | -------- |  | 0 | 0
12 |  |  |  |  | -------- | -------- |  | 0 | 0
14 | 20A-1P | SPARE |  |  | -------- | -------- |  | 0 | 0
16 | 20A-1P | SPARE |  |  | -------- | -------- |  | 0 | 0
18 | 20A-1P | RECEPTACLES |  | D | -------- | 5000 |  | 0 | 0
20 | 20A-1P | RECEPTACLES |  | D | 2340 | -------- |  | 2340 | 0
22 | SPACE | SPACE |  |  | -------- |  |  | 0 | 0
24 | 20A-2P | COUNTER RECEPTACLES |  | D | -------- | 5000 |  | 0 | 0
26 | 20A-2P |  |  | D | 2340 | -------- |  | 2340 | 0
28 | 20A-2P | SOFT SERVE RECEPTACLES |  | D | -------- | 2340 |  | 2340 | 0
30 | 20A-2P |  |  | D | -------- | -------- |  | 0 | 0
32 |  |  |  |  | 2000 | -------- |  | 0 | 0
34 | 30A-3P | SOFT SERVE RECEPTACLES 1 |  |  | -------- | 2000 |  | 0 | 0
36 |  |  |  |  | -------- | -------- |  | 0 | 0
38 |  |  |  |  | 3300 | -------- |  | 0 | 0
40 | 30A-3P | SOFT SERVE RECEPTACLES 2 |  |  | -------- | 3300 |  | 0 | 0
42 |  |  |  |  | -------- | -------- |  | 0 | 0
[8 empty] | 12820 | 0
[8 empty] | DIVERSITY | CONTINUOUS
CONDUCTOR AND CONDUIT SIZING DATABASE FOR THREE PHASE PANELS
SAMPLE DATABASE COPPER CONDUCTORS 75º C
[13 empty] | 1 |  | 2 |  | 3 |  | 4 |  |  | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[13 empty] | AMPS | SELECTED | #WIRES | SELECTED | WIRE | SELECTED | GND | SELECTED | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE | C-SIZE
[13 empty] | 75º C | CONDUCTOR | PER | NUMBER OF | SIZE | GROUND | WIRE | CONDUIT | 4W W/G | 3W | 3W W/G | 3W | 3W W/G | 4W | 4W W/G | 4W | 4W W/G
[14 empty] | SIZE | PHASE | CONDUCTORS |  | SIZE | SIZE | SIZE | THW | THW | THW | THHN | THHN | THW | THW | THHN | THHN
[13 empty] | 65 | 0 | 1 | 0 | #6 | 0 | #8 | 0 | 1 1/4" | 1" | 1" | 3/4" | 3/4" | 1" | 1 1/4" | 3/4" | 1"
[13 empty] | 85 | 0 | 1 | 0 | #4 | 0 | #8 | 0 | 1 1/4" | 1" | 1 1/4" | 1" | 1" | 1 1/4" | 1 1/4" | 1" | 1 1/4"
[13 empty] | 100 | #3 | 1 | 1 | #3 | #8 | #8 | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1" | 1" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
|  | LOAD CALCULATIONS FOR PANEL |  | "A" | [8 empty] | 115 | 0 | 1 | 0 | #2 | 0 | #6 | 0 | 1 1/2" | 1 1/4" | 1 1/4" | 1" | 1 1/4" | 1 1/4" | 1 1/2" | 1 1/4" | 1 1/4"
[13 empty] | 130 | 0 | 1 | 0 | #1 | 0 | #6 | 0 | 2" | 1 1/4" | 1 1/2" | 1 1/4" | 1 1/4" | 1 1/2" | 2" | 1 1/2" | 1 1/2"
|  | CONNECTED LOAD LINE L1 |  |  |  | 17180 | [6 empty] | 150 | 0 | 1 | 0 | #1/0 | 0 | #6 | 0 | 2" | 1 1/2" | 1 1/2" | 1 1/4" | 1 1/2" | 2" | 2" | 1 1/2" | 1 1/2"
|  | CONNECTED LOAD LINE L2 |  |  |  | 27040 | [6 empty] | 175 | 0 | 1 | 0 | #2/0 | 0 | #6 | 0 | 2" | 1 1/2" | 2" | 1 1/2" | 1 1/2" | 2" | 2" | 2" | 2"
[13 empty] | 200 | 0 | 1 | 0 | #3/0 | 0 | #6 | 0 | 2 1/2" | 2" | 2" | 1 1/2" | 2" | 2" | 2 1/2" | 2" | 2"
[13 empty] | 230 | 0 | 1 | 0 | #4/0 | 0 | #4 | 0 | 2 1/2" | 2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2" | 2 1/2"
|  | SUB TOTAL WATTS |  |  |  | 44220 | [6 empty] | 255 | 0 | 1 | 0 | 250 KCM | 0 | #4 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2" | 2 1/2" | 3" | 2 1/2" | 2 1/2"
[13 empty] | 285 | 0 | 1 | 0 | 300 KCM | 0 | #4 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
|  | RECEPTACLE LOAD |  |  | 12820 | [7 empty] | 310 | 0 | 1 | 0 | 350 KCM | 0 | #3 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
|  | LESS 1ST 10,000 WATTS |  |  | -10000 | [7 empty] | 335 | 0 | 1 | 0 | 400 KCM | 0 | #3 | 0 | 3" | 3" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[13 empty] | 380 | 0 | 1 | 0 | 500 KCM | 0 | #3 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | REMAINING WATTAGE |  |  | 2820 | [7 empty] | 400 | 0 | 1 | 0 | 500 KCM | 0 | #3 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | 50% OF THE REMAINING WATTAGE |  |  | 1410 | [7 empty] | 460 | 0 | 2 | 0 | #4/0 | 0 | #2 | 0 | 2 1/2" | 2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2" | 2 1/2"
[13 empty] | 510 | 0 | 2 | 0 | 250 KCM | 0 | #1 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 2 1/2" | 3" | 2 1/2" | 2 1/2"
|  | LESS RECEP DEMAND (PER Article 220-44 NEC) |  |  |  | -1410 | [6 empty] | 570 | 0 | 2 | 0 | 300 KCM | 0 | #1 | 0 | 3" | 2 1/2" | 2 1/2" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
[13 empty] | 620 | 0 | 2 | 0 | 350 KCM | 0 | #1/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
|  | CONTINUOUS LOAD |  |  | 0 | [7 empty] | 670 | 0 | 2 | 0 | 400 KCM | 0 | #1/0 | 0 | 3 1/2" | 3" | 3" | 2 1/2" | 3" | 3" | 3 1/2" | 3" | 3"
[5 empty] | X .25 | [7 empty] | 760 | 0 | 2 | 0 | 500 KCM | 0 | #1/0 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
[13 empty] | 855 | 0 | 3 | 0 | 300 KCM | 0 | #2/0 | 0 | 3" | 2 1/2" | 3" | 2" | 2 1/2" | 3" | 3" | 2 1/2" | 3"
|  | PLUS 25% OF THE CONTINUOUS LOAD |  |  |  | 0 | [6 empty] | 930 | 0 | 3 | 0 | 350 KCM | 0 | #2/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[13 empty] | 1005 | 0 | 3 | 0 | 400 KCM | 0 | #3/0 | 0 | 3 1/2" | 3" | 3" | 2 1/2" | 3" | 3" | 3 1/2" | 3" | 3"
[13 empty] | 1140 | 0 | 3 | 0 | 500 KCM | 0 | #3/0 | 0 | 3 1/2" | 3" | 3" | 3" | 3" | 3 1/2" | 3 1/2" | 3" | 3 1/2"
|  | SUB TOTAL |  |  |  | 42810 | [6 empty] | 1240 | 0 | 4 | 0 | 350 KCM | 0 | #4/0 | 0 | 3" | 2 1/2" | 3" | 2 1/2" | 2 1/2" | 3" | 3" | 3" | 3"
[14 empty] | #3 |  | 1 |  | #8 |  | 1 1/4"
|  | FACTOR | 0 |  |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0
[14 empty] | 0 |  | 0 |  | 0 |  | 0
|  | TOTAL WATTS |  |  |  | 42810 | [7 empty] | 0 |  | 0 |  | 0 |  | 0
[14 empty] | 0 |  | 0 |  | 0 |  | 0
AMPS
[5 empty] | = | 178.375 | [7 empty] | #3 |  | 1 |  | #8 |  | 1 1/4"
|  | LAST MODIFIED | 2022-09-01