## Critical Needs List
UCF Standards Critical Needs Checklist
PROJECT NAME:
UCF PROJECT #:
PHASE: |  | BY SUBMITTING THIS DOCUMENT, THE SUBMITTER AFFIRMS THAT ALL UCF STANDARDS HAVE BEEN REVIEWED AND INCORPORATED INTO THE PROJECT.
DATE:
DESIGNER: |  | REVISED 10-27-2021
CONTRACTOR:
SUBMITTER NAME:
INSTRUCTIONS:
1) At every phase milestone, this Critical Needs Checklist MUST be submitted with the design deliverables. Failure to submit this Critical Needs Checklist is grounds for considering a deliverable incomplete, and payment for the deliverable will be withheld until this checklist is submitted.
2) The designer must mark how specifically each item is addressed. For design items related to contract documents, specific references to specification sections and/or drawing sheets must be provided so that the UCF Project Manager can verify that the item has been adequately addressed. For some standard items related to processes, the designer can answer "ACKNOWLEDGED".
3) Prior to the start of construction, this Critical Needs Checklist MUST be submitted by the contractor. The contractor shall acknowledge each construction related item, or shall describe their plan to address each item (can refer to a separate document if necessary). For some standard items related to processes, the designer can answer "ACKNOWLEDGED".
4) Where an item has an accepted deviation, the designer must note "SEE APPROVED DEVIATION" and list the date of the approval. Approved deviations must also be included on sheets in design submittals.
Number | Description | Designer response | Contractor Response
CNA-1 | All construction specifications must be University project specific and based on the current version of the Standards. |  | N/A
CNA-2 | Firms under contract prior to May 2016 must review this edition for the most recent changes and evaluate any cost or time implications, if any, to their projects. These implications must be sent to the Project Manager, in writing, for action by the University. |  | N/A
CNB-1 | Any changes to in the approved facility program shall be modified by written recommendation for approval by the President. |  | N/A
CNB-2 | The Architect-of-Record is directed to work through the UCF Project Manager and simultaneously copy the Commissioning Agent (if applicable) on all communications and project coordination. |  | N/A
CNB-3 | The A/E shall provide the completed Critical Needs Checklist to the UCF Project Manager at every major deliverable, indicating where in the project documents the critical need is addressed. |  | N/A
CNB-4 | A project achieves “final completion” when: All building systems are complete, operating correctly, and approved by the Commissioning Authority and the Owner. All associated training is complete and approved by the Owner. All closeout documentation, including O&M Manuals, must be complete, in digital format, and have been approved by the Owner. As-builts of the completed project must be delivered to and accepted by the Owner. Utility cost responsibility is transferred to the Owner. The State Fire Marshal, the Building Official, and the University’s Department of Environmental Health & Safety must have inspected, tested, and approved the facility. The entire facility can be occupied and used for the designed purposes intended. All Facilities and Safety Departmental Directors have signed the certificate of final completion. All warranties must be accepted by the Owner to begin upon the date of final completion. All punch-list items must be completed.
CNB-5 | The Architect, with Owner approval, may issue the certificate of final completion only after all of the above conditions have been achieved.
CNC-1 | The work of the A/E will be reviewed by UCF to the extent necessary to establish conformance with authorized scope and applicable UCF design criteria. It is the responsibility of the A/E, acting in a professional capacity, to ensure the accuracy, completeness and correctness of project documents and details of the work. The A/E assumes full responsibility for the technical accuracy and professional adequacy of all work. |  | N/A
CNC1-2 | All designs must be consistent with the University’s Master Drainage Plan approved by the St. Johns River Water Management District (SJRWMD). The Architect and Engineer must comply with the design and installation requirements as established by the Florida Department of Environmental Protection. |  | N/A
CNC-2 | The use of untried materials is prohibited. Materials shall be used in a manner that will afford the maximum service at the lowest comparable cost.
CNC-3 | All major new construction and renovations must include progressive energy modeling. The energy modeling must be updated as the project progresses from programming through completed design. The energy model inputs, outputs, reports, and findings must be reviewed with the Commissioning Authority and the Director of Utilities & Energy Services prior to proceeding to the next phase of design. The initial model must be updated at the completion of the 100% Design Development phase, 50% Construction Document phase, and 100% Construction Document phase. |  | N/A
CNC-4 | CNC-4: All construction projects with any potential Utilities scope (list specific departments here e.g. CHW, HVAC, etc) shall be evaluated for utility impact. The designer of record shall complete and-submit the UCF Application for Concurrency Review and provide to the UCF Project Manager to submit prior to the 100% Design Development Phase submittal. Concurrency Certificate must be verified against 100% Construction Document Phase Submittal by the UCF Project Manager and issued prior to the start of construction.
CNC-5 | Implementation of a modular green roof and associated storm and condensate water capture must be considered and evaluated for all new University buildings. The decision to proceed with the design and development of the green roof, including additional requirements, will be made at the Advanced Schematic Design phase. Costs associated with the green roof must be presented to the UCF Project Manager for review. The evaluation must include the following requirements: The cost for the enhanced structure and roof membrane required for the green roof and associated walkways and safety features. The cost for the actual green roof system, apart from the other building elements, including installation. The effects of the green roof on the building’s roofing and drainage system, especially the roof warranty. The cost for any associated storm water system that may be required. The cost for the long-term maintenance of the green roof. A detailed summary of all costs for the proposed green roof system to quantify a total cost. A life cycle cost analysis using the total cost and the total energy savings. |  | N/A
CNC-6 | All equipment installed in UCF buildings will be designed for domestic use and will include any programming required to control such equipment. Overseas compatible equipment will not be accepted.
CNC-7 | The requirements contained in the UCF Professional Services Guide must be followed regarding final cleaning, adjusting of equipment, project record documents and close out procedures.
CN0-1 | Project drawings will be final and complete with all elements thoroughly checked and coordinated. |  | N/A
CN0-2 | Changes must not be made to the General or Special Conditions, without written approval from the Owner.
CN1-1 | All projects shall abide by the University Energy Sustainability Policy 3-111.1. This policy requires that all projects achieve a minimum LEED Gold certification and earn specific LEED credits.
CN1-2 | All designs must be consistent with the University’s Master Drainage Plan approved by the St. Johns River Water Management District (SJRWMD). The Architect and Engineer must comply with the design and installation requirements as established by the Florida Department of Environmental Protection. |  | N/A
CN1-3 | The A/E shall consult the Owner regarding priority of alternates. Only additive alternates shall be used. |  | N/A
CN1-4 | All projects shall be documented at major construction milestones such as foundation installation, slab pours, wall erection, MEP rough-in, etc. Photographs will be taken in each room, to include walls and above the ceiling. | N/A
CN1-5 | The Contractor shall provide a submittal review schedule and a sequence of submittal review to the Owner. | N/A
CN1-6 | Lock out/tag out procedures are required to be used in all campus facilities. | N/A
CN1-7 | All Contractors shall attend a one-hour annual session covering UCF Environmental Management System construction-specific components and provide certification that the information has been transmitted to all ffected employees and sub-Contractors. | N/A
CN1-8 | A quality control and quality assurance plan shall be provided and implemented by the Contractor. | N/A
CN1-9 | All testing must be performed by the Contractor unless otherwise directed by the Owner.
CN1-10 | Fire lanes must be provided to all structures.
CN1-11 | Prior to the start of construction, a plan of the existing on-campus streets and roadways that will be used shall be submitted to the UCF Project Manager. | N/A
CN1-12 | Fill soils kept on site during construction shall remain covered or contained at all times. | N/A
CN1-13 | The Contractor shall remove mud and spillage from public and University streets on a daily basis. Failure to clean streets daily shall result in streets being cleaned by the Owner at the Contractor’s expense. | N/A
CN1-14 | A detailed plan regarding the requirements for building systems start-up shall be provided by the Contractor. This is in addition to, and separate from, full commissioning. | N/A
CN1-15 | An ACCEPTABLE record set of dated construction documents, incorporating changes during construction, must be received by the University prior to final payment to the A/E and Contractor. For all field changes made during construction, the contracted professional is responsible for the accuracy of information placed on the record documents.
CN1-16 | It is the responsibility of the A/E to incorporate these Standards into the specifications or other contract documents, and to secure compliance of the Contractor with these Standards, including changes in design and specifications during construction incorporated into “record set” conditions. |  | N/A
CN1-17 | In cases of multiple installation of identical equipment, only one manual submitted for the identical equipment is necessary, but model and serial numbers of the equipment shall be listed.
CN1-18 | Manufacturers’ maintenance instructions shall include schedules showing proper time intervals for all manufacturers’ routine maintenance (e.g., lubrication, adjustment, calibration, or checking). The Contractor shall consolidate manufacturers’ schedules with a single master schedule of required maintenance. | N/A
CN1-19 | Installation of systems that are known to be obsolete or are soon to be obsolete shall not be specified. |  | N/A
CN1-20 | An all-inclusive Warranty Matrix that clearly identifies start and end dates of the Contractor’s warranty and the manufacturer’s warranty shall be provided by the Contractor for all equipment. All warranties shall begin at Substantial Completion. | N/A
CN1-21 | All name plate data shall include manufacturer, model number, serial number, date of installation, room number (location), and operating parameters. This data shall be provided in ODBC database format (MS Excel or Access). | N/A
CN1-22 | A two-year minimum warranty is required on all building components. The roof system requires a twenty-five year no dollar limit (NDL) warranty.
CN2-1 | All Contractors shall attend a one-hour annual session covering UCF Environmental Management System construction-specific components. Contractors shall certify that provided information has been transmitted to all affected employees and subcontractors. | N/A
CN3-1 | Unpainted, precast concrete shall be coated with a siloxane water repellent to reduce surface absorbency.
CN4-1 | Tinted or colored mortar is prohibited except on walls with all cast stone.
CN4-2 | Brick cavity walls shall have a 2” minimum air gap between the back of the brick and the next wall/insulation surface in the wall assembly.
CN4-3 | New CMU shall be placed in a running bond pattern. Stack bond in load-bearing walls is prohibited.
CN4-4 | Glass unit masonry may not be used.
CN4-5 | Do not sand blast or acid wash brick surfaces.
CN4-6 | Cast stone shall be coated with a siloxane water repellent to reduce surface absorbency.
CN5-1 | CN5-1: All structural and miscellaneous steel on all UCF projects must be shop primed. All primed iron and steel beams must be touched-up or corrected at the jobsite.
CN5-2 | All exterior handrails and guardrails shall be brushed aluminum or stainless steel pipe. Painted exterior handrails and guardrails are prohibited.
CN5-3 | For interior spaces, the guardrails and handrails shall be an all-aluminum or all-stainless steel system. Aluminum handrails shall be brushed aluminum. Painting is prohibited.
CN6-1 | Wood materials shall not be used for any structural elements.
CN6-2 | Wood handrails are prohibited.
CN7-1 | The entire site must be graded to provide positive drainage away from the building. Finish floor elevation must be set to prohibit flooding in a 100 year storm condition.
CN7-2 | The use of stucco is prohibited.
CN7-3 | The design prepared by the A/E shall adhere to the Facilities and Safety Memorandum: Roof Systems, found on the Facilities Planning and Construction website. |  | N/A
CN7-4 | The Architect, Engineer, and Construction Manager must coordinate with the University’s Building Envelope consultant.
CN7-5 | The 100% construction document will include complete roofing documentation. |  | N/A
CN7-6 | The 50% construction documents shall include complete roofing specifications and details. |  | N/A
CN7-7 | Roof drainage must be tied into the underground storm water system unless a local cistern is incorporated into the project. If a cistern is used, overflow must be directed to the campus storm water system.
CN7-8 | Hot mop applied roof products are prohibited.
CN7-9 | All thermal insulation shall be installed at the roof deck. Insulation laid on suspended ceilings is not permitted.
CN7-10 | All roofs shall have three (3) -foot wide continuous walking pads from points of access to and around all equipment, shall be an integral assembly to the roof membrane, shall meet all required wind loads, shall be approved by the manufacturer, and shall be included in the roof warranty. Modified bitumen systems path shall be minimum 36" and single ply membrane systems shall be minimum 30" in width. Additional width is preferres at roof access points, landings, and equipment service areas.
CN7-11 | The use of curb-mounted roof equipment is not permitted, except as follows: fume hood and hood exhaust, toilet exhaust, and smoke exhaust, or as approved by the UCF Project Manager. Projects for re-roofing buildings that currently have roof-mounted equipment shall include removing and relocating such equipment.
CN7-12 | Traditional skylights are not permitted.
CN7-13 | Interior gutter systems for roof drainage are prohibited.
CN7-14 | All roofing details shall be reviewed and approved by the Owner, prior to the pre-installation conference.
CN7-15 | Within a period of three (3) to six (6) months after the final completion, an aerial infrared scan of the roof system must be performed by a third party vendor not affiliated with the roofing contractor and the results transmitted to the owner. The aerial scan and results report shall meet the documentation requirements of the Infraspection Institute for infrared inspection of insulated roofs.
CN7-16 | Metal wall panel systems shall be detailed and specified with continuous vapor barrier systems, flashing, and weeps so that water will not accumulate within the wall system.
CN7-17 | Single ply membranes are to be used on roofs with minimal equipment and traffic. All other roofs must be modified bitumen, with Energy Star compliant cap sheet. Hot mop applied roof products are prohibited.
CN7-18 | Caulking must meet the ASTM requirements for the system designed, have the maximum warranty available and be reviewed by the UCF Project Manager.
CN7-19 | Sealants and caulking shall have a minimum twenty (20)-year warranty.
CN7-20 | Sealants and caulking used for interior retail applications are required to have a minimum five (5)-year warranty. All other sealants and caulking shall have a minimum twenty (20)-year warranty.
CN8-1 | Exterior doorways shall be explicitly designed against water intrusion into the building. Adequate positive slope away from the doorway, with trench drains and/or overhangs, shall be provided. Public entry doors shall be recessed or located under an overhang at a minimum of four (4) feet to prevent water intrusion. Glass awnings are prohibited. |  | N/A
CN8-2 | Review Annual Door Opening Inspection requirements according to NFPA 101, and accommodate in design. |  | N/A
CN8-3 | Coordinate door opening force and closer timing with ADA requirements. | N/A
CN8-4 | Doors equipped with an opening device must be in full compliance with current ANSI and ADA requirements.
CN8-5 | Perimeter of building openings shall receive sealant, sealant and backer rod, or weather-stripping.
CN8-6 | Exterior wood doors are prohibited.
CN8-7 | All exterior roll-up doors must be insulated and manually operated with an integral locking device.
CN8-8 | Regular, side-hinged type doors requiring minimal annual maintenance shall be specified for all applications.
CN8-9 | Operable windows are prohibited.
CN8-10 | The types of glass and locations used must be reviewed by the University Building Envelope Consultants and approved by the Owner.
CN8-11 | The finish hardware schedule will be provided to UCF by the Architect with the Design Development Phase submittal.
CN8-12 | All areas must be accessible with a UCF great grand master key.
CN9-1 | The selection of materials shall be assessed for long-range, life-cycle cost analysis. |  | N/A
CN9-2 | The Architect or Interior Designer shall provide a non-returnable, detailed interior color board, including all paints, wall tiles, grouts, wood door finishes, millwork, cabinet/countertops, and any other publicly visible interior finishes. Preliminary finish options (paint, base carpet, tile, toilet partitions, exterior materials) shall be presented at the Design Development phase workshop. The final color board shall be submitted and approved by completion of the 50% Construction Documents Phase.
CN9-3 | Samples of ALL finishes and finishing material must be submitted to the Owner for approval PRIOR TO ORDERING.
CN9-4 | Gypsum wall board shall not be installed until the building is adequately dried-in. | N/A
CN9-5 | All rolled carpet must be direct glue down.
CN9-6 | Carpeting in stairways, break rooms, and food service areas is prohibited.
CN10-1 | All assigned rooms shall have University standard signage denoting the room number.
CN10-2 | All exterior building signage must follow the UCF Marketing Guidelines. The Gotham font shall be used for all exterior building signage.
CN10-3 | Toilet partitions must be mounted to the structure with independent overhead reinforcements and wall brackets.
CN10-4 | UCF will provide, and the Contractor will install: Soap dispensers, toilet tissue dispensers, and paper towel dispensers Free-standing, stainless steel waste receptacles
CN11-1 | All buildings must be provided with grade-level vehicular access.
CN11-2 | A three (3)-inch floor drain with trap primer and integral funnel shall be provided at each emergency eyewash and shower equipment station. The adjacent floor shall be sloped to drain.
CN11-3 | Laboratory hoods and associated exhaust or supply system shall be tested and balanced again six (6) months after the date of occupancy. The report shall include adjustments made or recommended, fan curve performance efficiency, vortex behavior, and face velocity.
CN11-4 | Equipment needed to provide facilities operational support to the building will take priority in funding over general building furnishings and equipment.
CN11-5 | Central vacuum cleaning systems are prohibited.
CN11-6 | A two (2) feet by five (5) feet setback shall be provided to accommodate Owner-provided recycling bins in a public area corridor of each floor.
CN12-1 | Bases for all casework, hoods, or similar border areas at fixed laboratory furnishings shall be feet mounted for cleaning underneath or equipped with a liquid tight seal at the floor to prevent spills from seeping under adjacent surfaces.
CN12-2 | Furnishings and equipment placed in close proximity to wet areas (sinks, safety showers, etc.) shall be water-resistant.
CN14-1 | New installations shall be gearless traction elevators driven by AC electric motors.
CN14-2 | Certificates must be mounted in the elevator cab before the building can be occupied. | N/A
CN21-1 | In determining the adequacy of the existing water source to meet the required fire flow, it is the responsibility of the system designer to perform the necessary site flow tests, in coordination with the UCF Project Manager and witnessed by the Owner. Timing shall be coordinated at peak demand to reflect typical conditions and include a suitable factor of safety using historic data.
CN21-2 | All system drains and test connections shall be hard-piped to a termination point outside of the building at grade, away from public view or access ways, and arranged to avoid damaging landscaping.
CN21-3 | Doors exiting clean agent-protected areas shall have vision panels, swing in the direction of egress, and include panic hardware.
CN21-4 | The system specification shall require the vendor to provide a maximum price for the services below to be guaranteed for a minimum of five years.
CN21-5 | Design shall include a contingency plan for ventilation of the protected area and restarting of HVAC after discharge.
CN21-6 | All piping shall be thoroughly cleaned, reamed, blown clear, and swabbed with suitable solvents to remove burrs, mill varnishes, and cutting oils before assembly. Prior to hanging the pipe, approval by the UCF Project Manager is required.
CN21-7 | Agent tanks shall be new and dated within six months of system acceptance.
CN22-1 | The design of the water distribution system on multi-level buildings shall provide an easily accessible capability of cutting off all water supplies on each floor level and each restroom, independently of the other floors and restrooms.
CN22-2 | All valves must be of American manufacture.
CN22-3 | Butterfly valves are not permitted in potable water or fire suppression systems.
CN22-4 | Lift station alarm systems must match existing campus SCADA Reporting System.
CN22-5 | Each pumping station control system must match existing campus infrastructure.
CN23-1 | A 25-year life cycle cost analysis (LCCA) shall be provided for the mechanical systems for each project where total cooling capacity exceeds 40 tons. At least three (3) schemes must be included in the analysis. One (1) of the schemes considered must be a central system, such as the campus district cooling loop. The three schemes must be presented to the UCF Director of Utilities and Energy Services for review.
CN23-2 | When a mechanical room is located in close proximity to classrooms or office, soundproofing is required. Close proximity is defined as adjacent to or across a hallway of not more than 6 feet width from the mechanical room.
CN23-3 | Clearance around mechanical equipment, where applicable, must meet or exceed manufacturers required clearance. Indiacte clearances for all mechanical equipment on drawings, including full coil replacements.
CN23-4 | All projects involving addition of, removal of or modification to any HVAC system shall utilize the UCF-provided Systems Usage Plan matrix. The contractor is to coordinate activities and responsibilities on this matrix document in conjunction with their project schedule. The purpose is to clearly communicate to all project stakeholders who are responsible for which systems at which times, and when systems will be demolished, disabled, installed, startup, TAB, Cx and turnover as well as documenting needs for temporary heating or cooling.
CN23-5 | All projects involving addition of, removal of or modification to any HVAC system shall have a pre-TAB conducted of the entire system(s), as determined by UES, that will be affected by the project to fully understand existing conditions and performance characteristics that may impact the successful completion of the project and the existing systems to remain. | N/A
CN23-6 | All new or replacement chilled water piping systems shall be chemically cleaned prior to connection to the main chilled water system by requesting coordination of treatment with the UES Water Treatment Vendor. Failure to follow the hydronic flushing procedural instructions by flushing detergent, dirt, rust, debris and other detritus from the piping into the hydronic chilled water or heating hot water coils will result in rejection of acceptance of that equipment, and the contractor shall be responsible for replacing the impacted coils at their own expense and shall be responsible for liquidated damages resulting in project delays resulting from these actions. | N/A
CN23-7 | Only chemicals approved by UCF UES shall be introduced into the UCF chilled water piping system. Raw or potable water shall not be introduced into the campus chilled water piping system.
CN23-8 | All internal parts on tapping machines, such as cutting heads etc., shall be disinfected in compliance with AWWA C601 and C900, prior to making any tap. The cutout shall be provided to the Owner.
CN23-9 | Rigid duct board insulation to insulate sheet metal ductwork is prohibited outside of mechanical rooms. | N/A
CN23-10 | Rigid duct board insulation over sheet metal shall be used in all mechanical rooms.
CN23-11 | Return air plenums using floor and/or an exterior wall as side of the enclosure are prohibited.
CN23-12 | During the construction phase, filters shall be replaced when the pressure drop across the filter exceeds ½” of water column.
CN23-13 | All filters shall be replaced on the day of final completion. The Contractor shall provide the Owner two additional sets of filters for each unit.
CN23-14 | The contractor shall provide the Owner with two additional sets of belts for each belt-driven unit.
CN23-15 | The Contractor shall perform cleaning of all air handler units, including coils and ductwork just prior to final completion filter replacement.
CN23-16 | The Contractor shall perform cleaning of all DX equipment, including evaporator and condenser coils, just prior to final completion of filter replacement.
CN26-1 | Metal conduit of a minimum of three-quarters of an inch (3/4”) with compression fittings shall be used in the interiors of all buildings except in walls as listed below.
CN26-2 | All conductors in cabinets must be carefully formed and harnessed so that each conductor drops off directly opposite to its terminal.
CN26-3 | Dedicated rooms shall be provided for electrical. Each room’s access must be located directly off a main corridor or common area.
CN26-4 | All mains, feeders, and branch circuit panels shall be of the bolt-on circuit breaker type. A neutral wire is required for all circuits.
CN26-5 | The entire front trim of panelboards must be hinged to the box and with a standard door within the hinged trim cover. Trims must cover all live parts and must have no exposed hardware.
CN26-6 | The generator cannot be ordered until an air construction permit is obtained from OCEPD by EH&S.
CN26-7 | The State Fire Marshal or his designated representative shall be present to witness the on-site acceptance and load-bank testing. | N/A
CN26-8 | Automated light harvesting technology shall be installed in all spaces which receive natural lighting.
CN26-9 | Emergency lighting and illuminated exit signage shall be on centralized circuits to facilitate monthly testing All exit signage fixtures shall be LED-type. Radioactive source signage is prohibited.
CN28-1 | Installation of any system in no way implies continued maintenance service contracts with the installing Contractor. The installed system shall have replacement parts that are readily obtainable and can be serviced by a third-party, licensed vendor who is Owner-selected by a separate bid process. Such service shall not have an effect on warranties.
CN28-2 | The system shall be a recent model for which replacement parts and local service are guaranteed to be readily available for a minimum of ten (10) years from the date of installation.
CN28-3 | If more than 50% of an existing fire alarm system is affected or it is more than ten years old, it shall be upgraded to the current standard.
CN28-4 | Each fire alarm system on the main campus shall be connected to the UCF Campus Receiving Station for fire alarm monitoring at the Police Building.
CN28-5 | In addition to where required by code, all buildings meeting the following criteria shall be designed with a fire alarm including voice evacuation throughout (EVAC), and shall be connected to the campus Mass Notification System (MNS): Any facility with 300 or more occupants or capable of being expanded to 300 or more; Any facility with 50 or more occupants above or below the level of exit discharge; Any facility with hazardous processes, materials, or laboratories; Any facility deemed so in need by the UCF Emergency Manager, due to special circumstances. Where a fire alarm system is not required but a Mass Notification System is deemed essential, a separate voice notification system is required. See the Mass Notification System section for further details.
CN28-6 | Atriums and similar spaces are to be avoided when possible due to the necessity for these complicated smoke evacuation and control systems as provided by code. Where such systems are installed, the engineer of record shall provide a comprehensive system Operations and Maintenance manual for approval prior to permitting. Such manual shall: Identify all sequences of operations and all associated equipment and systems (HVAC, fire alarm, sprinkler, doors, dampers, fans, etc.) with drawings, cut sheets, and identification labels that will also be installed on each applicable component. Include a walk-through and balance protocol, indicating the initial acceptance testing sequence for all components on all power sources, with a comprehensive report matrix. The matrix will be executed and filled out by the installer and approved by the engineer of record prior to Certificate of Occupancy. Include a reoccurring service test and balance and maintenance protocol matrix to be used by the Owner for semiannual and annual services and comparison to the original acceptance testing.
CN28-7 | All initiation device (IDC), notification appliance (NAC), and signaling line (SLC) circuits must be Class A (NFPA Style Z), with no T-Tapping or spider-webbed type circuitry.
CN28-8 | System wiring shall be in red raceways (Allied “True Color” or equivalent), minimum ¾” EMT.
CN28-9 | All conductors in cabinets shall be carefully formed and harnessed so that each conductor drops off directly opposite to its terminal.
CN28-10 | The fire alarm system shall be successfully inspected, demonstrated, and approved by the Engineer of Record prior to requesting inspection by the State Fire Marshal.
CN28-11 | All new facilities must be provided with a means of Emergency Mass Notification.
CN31-1 | Any existing tree(s) indicated to remain (per approved construction plans) that are damaged or removed during construction must be replaced with new tree(s) of similar size.
CN31-2 | Clean topsoil and other clean excavated soils shall not be removed from the campus and shall be stored at a site designated by the UCF Project Manager. All testing and transportation of excavated material is the responsibility of the Contractor. All soil and appropriate testing shall be approved by Landscape and Natural Resources prior to transportation.
CN31-3 | Soil that is compromised with debris, organic and inorganic, as determined by testing, shall be removed from the campus.
CN32-1 | All exterior seating and retaining walls must be designed with integral anti-skateboarding devices.
CN32-2 | All plant species shall comply with Florida Friendly™ Standards. No shrubbery or trees shall be installed around or in front of light poles, transformers and switch gear, or fire service equipment. Future plant growth shall be considered relative to signage, lighting, and entryway features.
CN33-1 | The Prime Contractor shall notify Sunshine 811 prior to excavation of proposed area and provide the utility with the address and major street intersections or references to natural or man-made landmarks, and will identify in white paint or stakes the proposed area. | N/A
CN33-2 | The location of fire hydrants must be determined by FFPC and approved by the Owner.
CN33-3 | Backflow preventers must be manufactured by Wilkins. Provide type RPZ, model 975 XL for 2” lines smaller, or model 375 with OS&Y valves for 3” lines or larger for building installations. Provide type 350DA on fire mains, and type DC, model 950 XL of irrigation systems. For 2” or smaller, the pipe supporting the device must be copper. For 3”and larger, the pipe supporting the device must be ductile iron. No backflow preventers between 2” and 3” are permitted.
| Architect/Engineer Signature | Date
| UCF Project Manager Signature | Date